## Sheet1
CATERPILLAR® POWER PRODUCTS
LOAD BANK TEST REPORT
(317) 545-2151
CUSTOMER: | USED EQUIP | [5 empty] | SITE: |  | HQ YARD | [5 empty] | Job#
Pre-Start up Checks: | [12 empty] | Test Date: | 2025-05-08
| X | 1. Eng. Oil Level |  | X | 4. Safety ground connected | [7 empty] | Tested By: | Dillon Brown
| X | 2. Coolant Level |  | X | 5. Circuit breaker open (off) | [7 empty] | Title: | TECHNICIAN
| X | 3. Generator and load bank connected for proper volts | [10 empty] | Tested At: | 100%
[12 empty] | Ambient Temp: |  | 69° F
Engine Model: |  |  | 3412 | [5 empty] | Serial Number: | 2WJ02432 |  |  |  | KW: | 800
Generator Mfg/Model: |  |  | SR-4B | [5 empty] | Serial Number: | 7AJ01759
Control Panel Mfg: |  |  | CAT | [5 empty] | Serial Number: | EMCP II
Engine Safeties - Operational Test and/or Set Points:
Low Oil Pressure: |  | 30 |  | PSI |  | Over-speed: |  | 2120 |  |  |  |  | RPM: | 1800
Hi Water Temp: |  | 225 |  | F |  | Hours Before: |  | 296 |  |  |  | Hours After: |  | 297
Test Load/Duration: |  | 1 Hr | [10 empty] | 15 | Min. Record Intervals
TIME | VOLTS |  |  |  |  | AMPS |  |  |  |  | FREQ HZ | LOAD KW | COOL TEMP F | Lube Oil | FUEL PRESS | % OF LOAD
| 1 |  | 2 | 3 |  | 1 | 2 |  | 3
14:50 | 480 |  | 481 | 479 |  | 0 | 0 |  | 0 |  | 60 | 0 | 172 | 78 | 45 | 0%
14:55 | 480 |  | 480 | 479 |  | 265 | 264 |  | 265 |  | 60 | 220.3104 | 175 | 73 | 43 | 27.54%
15:00 | 481 |  | 480 | 480 |  | 501 | 506 |  | 503 |  | 60 | 421.5446 | 178 | 71 | 41 | 52.69%
15:05 | 481 |  | 482 | 480 |  | 685 | 690 |  | 688 |  | 60 | 576.0286 | 181 | 68 | 40 | 72%
15:20 | 482 |  | 484 | 483 |  | 927 | 931 |  | 926 |  | 60 | 780.4461 | 187 | 64 | 37 | 97.56%
15:35 | 482 |  | 481 | 482 |  | 926 | 930 |  | 927 |  | 60 | 776.3863 | 187 | 64 | 35 | 97.05%
15:50 | 483 |  | 483 | 482 |  | 927 | 931 |  | 927 |  | 60 | 778.8336 | 185 | 64 | 35 | 97.35%
16:05 | 481 |  | 484 | 483 |  | 927 | 930 |  | 928 |  | 60 | 779.6078 | 185 | 64 | 35 | 97.45%
16:10 | 480 |  | 481 | 479 |  | 0 | 0 |  | 0 |  | 60 | 0 | 171 | 74 | 45 | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | #DIV/0!
Customer Witness Acceptance: | [7 empty] | MacAllister Engine Power Approval:
By: | [7 empty] | By:
Title: | [7 empty] | Title: |  | TECH
SMM/MEP/072800 | [15 empty] | Page 1 of | 1