## Sheet1
CATERPILLAR® POWER PRODUCTS
LOAD BANK TEST REPORT
(317) 545-2151
CUSTOMER: | USED EQUIP | [5 empty] | SITE: |  | HQ YARD | [5 empty] | Job# | 9801212
Pre-Start up Checks: | [12 empty] | Test Date: | 2025-04-16
| X | 1. Eng. Oil Level |  | X | 4. Safety ground connected | [7 empty] | Tested By: | Dillon Brown
| X | 2. Coolant Level |  | X | 5. Circuit breaker open (off) | [7 empty] | Title: | TECHNICIAN
| X | 3. Generator and load bank connected for proper volts | [10 empty] | Tested At: | 100%
[12 empty] | Ambient Temp: |  | 39°F
Engine Model: |  |  | C27 | [5 empty] | Serial Number: | DWB01633 |  |  |  | KW: | 800
Generator Mfg/Model: |  |  | SR4B | [5 empty] | Serial Number: | AFR03123
Control Panel Mfg: |  |  | CAT | [5 empty] | Serial Number: | EMCP 3.2
Engine Safeties - Operational Test and/or Set Points:
Low Oil Pressure: |  | 30 |  | PSI |  | Over-speed: |  | 2120 |  |  |  |  | RPM: | 1800
Hi Water Temp: |  | 225 |  | F |  | Hours Before: |  | 342 |  |  |  | Hours After: |  | 343
Test Load/Duration: |  | 1 Hr | [10 empty] | 15 | Min. Record Intervals
TIME | VOLTS |  |  |  |  | AMPS |  |  |  |  | FREQ HZ | LOAD KW | COOL TEMP F | Lube Oil | FUEL PRESS | % OF LOAD
| 1 |  | 2 | 3 |  | 1 | 2 |  | 3
8:35 | 479 |  | 482 | 480 |  | 0 | 0 |  | 0 |  | 60 | 0 | 151 | 80 | 113 | 0%
8:50 | 480 |  | 482 | 479 |  | 927 | 932 |  | 930 |  | 60 | 778.056 | 181 | 63 | 113 | 97.26%
9:05 | 480 |  | 483 | 479 |  | 926 | 931 |  | 931 |  | 60 | 778.8336 | 181 | 63 | 112 | 97.35%
9:20 | 479 |  | 482 | 480 |  | 926 | 930 |  | 929 |  | 60 | 776.3863 | 181 | 63 | 112 | 97.05%
9:35 | 479 |  | 483 | 478 |  | 924 | 930 |  | 930 |  | 60 | 777.9971 | 181 | 63 | 112 | 97.25%
9:40 | 480 |  | 482 | 479 |  | 0 | 0 |  | 0 |  | 60 | 0 | 174 | 70 | 112 | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | #DIV/0!
Customer Witness Acceptance: | [7 empty] | MacAllister Engine Power Approval:
By: | [7 empty] | By:
Title: | [7 empty] | Title: |  | TECH
SMM/MEP/072800 | [15 empty] | Page 1 of | 1