## Sheet1
CATERPILLAR® POWER PRODUCTS
LOAD BANK TEST REPORT
(317) 545-2151
CUSTOMER: | USED EQUIP | [5 empty] | SITE: |  | HQ YARD | [5 empty] | Job# | 9801148
Pre-Start up Checks: | [12 empty] | Test Date: | 2025-04-18
| X | 1. Eng. Oil Level |  | X | 4. Safety ground connected | [7 empty] | Tested By: | Dillon Brown
| X | 2. Coolant Level |  | X | 5. Circuit breaker open (off) | [7 empty] | Title: | TECHNICIAN
| X | 3. Generator and load bank connected for proper volts | [10 empty] | Tested At: | 100%
[12 empty] | Ambient Temp: |  | 62°F
Engine Model: |  |  | C27 | [5 empty] | Serial Number: | DWB01632 |  |  |  | KW: | 800
Generator Mfg/Model: |  |  | SR4B | [5 empty] | Serial Number: | AFR03124
Control Panel Mfg: |  |  | CAT | [5 empty] | Serial Number: | EMCP 3.2
Engine Safeties - Operational Test and/or Set Points:
Low Oil Pressure: |  | 30 |  | PSI |  | Over-speed: |  | 2120 |  |  |  |  | RPM: | 1800
Hi Water Temp: |  | 225 |  | F |  | Hours Before: |  | 342 |  |  |  | Hours After: |  | 343
Test Load/Duration: |  | 1 Hr | [10 empty] | 15 | Min. Record Intervals
TIME | VOLTS |  |  |  |  | AMPS |  |  |  |  | FREQ HZ | LOAD KW | COOL TEMP F | Lube Oil | FUEL PRESS | % OF LOAD
| 1 |  | 2 | 3 |  | 1 | 2 |  | 3
9:35 | 481 |  | 482 | 479 |  | 0 | 0 |  | 0 |  | 60 | 0 | 162 | 82 | 104 | 0%
9:50 | 482 |  | 483 | 479 |  | 926 | 935 |  | 929 |  | 60 | 782.1799 | 185 | 61 | 105 | 97.77%
10:05 | 481 |  | 482 | 478 |  | 925 | 934 |  | 928 |  | 60 | 779.7256 | 185 | 61 | 105 | 97.47%
10:20 | 482 |  | 483 | 479 |  | 925 | 933 |  | 929 |  | 60 | 780.5067 | 185 | 61 | 105 | 97.56%
10:35 | 482 |  | 482 | 477 |  | 925 | 934 |  | 929 |  | 60 | 779.7256 | 185 | 60 | 104 | 97.47%
10:40 | 481 |  | 483 | 479 |  | 0 | 0 |  | 0 |  | 60 | 0 | 176 | 68 | 103 | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | #DIV/0!
Customer Witness Acceptance: | [7 empty] | MacAllister Engine Power Approval:
By: | [7 empty] | By:
Title: | [7 empty] | Title: |  | TECH
SMM/MEP/072800 | [15 empty] | Page 1 of | 1