## Sheet1
CATERPILLAR® POWER PRODUCTS
LOAD BANK TEST REPORT
(317) 545-2151
CUSTOMER: | USED EQUIP | [5 empty] | SITE: |  | HQ YARD | [5 empty] | Job#
Pre-Start up Checks: | [12 empty] | Test Date: | 2025-05-19
| X | 1. Eng. Oil Level |  | X | 4. Safety ground connected | [7 empty] | Tested By: | Dillon Brown
| X | 2. Coolant Level |  | X | 5. Circuit breaker open (off) | [7 empty] | Title: | TECHNICIAN
| X | 3. Generator and load bank connected for proper volts | [10 empty] | Tested At: | 100%
[12 empty] | Ambient Temp: |  | 62°F
Engine Model: |  |  | DEFK-5763542 | [5 empty] | Serial Number: | F060936360 |  |  |  | KW: | 500
Generator Mfg/Model: |  |  | NEWAGE | [5 empty] | Serial Number: | S111266-01
Control Panel Mfg: |  |  | Power Command | [5 empty] | Serial Number: | PCC 3201
Engine Safeties - Operational Test and/or Set Points:
Low Oil Pressure: |  | 30 |  | PSI |  | Over-speed: |  | 2120 |  |  |  |  | RPM: | 1800
Hi Water Temp: |  | 225 |  | F |  | Hours Before: |  | 499 |  |  |  | Hours After: |  | 500
Test Load/Duration: |  | 1 Hr | [10 empty] | 15 | Min. Record Intervals
TIME | VOLTS |  |  |  |  | AMPS |  |  |  |  | FREQ HZ | LOAD KW | COOL TEMP F | Lube Oil | FUEL PRESS | % OF LOAD
| 1 |  | 2 | 3 |  | 1 | 2 |  | 3
11:45 | 480 |  | 481 | 479 |  | 0 | 0 |  | 0 |  | 60 | 0 | 154 | 46 | 289 | 0%
11:50 | 481 |  | 482 | 480 |  | 143 | 143 |  | 139 |  | 60 | 119.3798 | 178 | 44 | 295 | 23.88%
11:55 | 480 |  | 482 | 480 |  | 322 | 323 |  | 321 |  | 60 | 269.6482 | 180 | 41 | 295 | 53.93%
12:00 | 481 |  | 482 | 480 |  | 443 | 445 |  | 444 |  | 60 | 371.4967 | 181 | 39 | 292 | 74.3%
12:15 | 480 |  | 482 | 480 |  | 623 | 624 |  | 626 |  | 60 | 522.5998 | 185 | 38 | 291 | 104.5%
12:30 | 481 |  | 482 | 480 |  | 623 | 625 |  | 624 |  | 60 | 521.765 | 187 | 38 | 291 | 104.4%
12:45 | 480 |  | 481 | 480 |  | 622 | 624 |  | 626 |  | 60 | 521.5156 | 186 | 38 | 291 | 104.3%
13:00 | 480 |  | 481 | 479 |  | 623 | 626 |  | 625 |  | 60 | 521.5156 | 186 | 39 | 290 | 104.3%
13:05 | 480 |  | 481 | 480 |  | 0 | 0 |  | 0 |  | 60 | 0 | 177 | 40 | 289 | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | #DIV/0!
Customer Witness Acceptance: | [7 empty] | MacAllister Engine Power Approval:
By: | [7 empty] | By:
Title: | [7 empty] | Title: |  | TECH
SMM/MEP/072800 | [15 empty] | Page 1 of | 1