## Sheet1
CATERPILLAR® POWER PRODUCTS
LOAD BANK TEST REPORT
(317) 545-2151
CUSTOMER: | USED EQUIP | [5 empty] | SITE: |  | HQ YARD | [5 empty] | Job# | 10001372
Pre-Start up Checks: | [12 empty] | Test Date:
| X | 1. Eng. Oil Level |  | X | 4. Safety ground connected | [7 empty] | Tested By: | Dillon Brown
| X | 2. Coolant Level |  | X | 5. Circuit breaker open (off) | [7 empty] | Title: | TECHNICIAN
| X | 3. Generator and load bank connected for proper volts | [10 empty] | Tested At: | 100%
[12 empty] | Ambient Temp: |  | 60°F
Engine Model: |  |  | 3406 | [5 empty] | Serial Number: | 4ZR03849 |  |  |  | KW: | 300
Generator Mfg/Model: |  |  | SR4B | [5 empty] | Serial Number: | 9CR01280
Control Panel Mfg: |  |  | CAT | [5 empty] | Serial Number: | EMCP II
Engine Safeties - Operational Test and/or Set Points:
Low Oil Pressure: |  | 30 |  | PSI |  | Over-speed: |  | 2120 |  |  |  |  | RPM: | 1800
Hi Water Temp: |  | 225 |  | F |  | Hours Before: |  | 357 |  |  |  | Hours After: |  | 358
Test Load/Duration: |  | 1 Hr | [10 empty] | 15 | Min. Record Intervals
TIME | VOLTS |  |  |  |  | AMPS |  |  |  |  | FREQ HZ | LOAD KW | COOL TEMP F | Lube Oil | FUEL PRESS | % OF LOAD
| 1 |  | 2 | 3 |  | 1 | 2 |  | 3
9:20 | 481 |  | 478 | 480 |  | 0 | 0 |  | 0 |  | 60 | 0 | 142 | 67 |  | 0%
9:25 | 480 |  | 478 | 481 |  | 89 | 90 |  | 89 |  | 60 | 74.9783 | 172 | 65 |  | 24.99%
9:30 | 483 |  | 479 | 482 |  | 178 | 178 |  | 178 |  | 60 | 148.907 | 176 | 60 |  | 49.64%
9:35 | 484 |  | 478 | 482 |  | 269 | 270 |  | 270 |  | 60 | 226.3378 | 178 | 58 |  | 75.45%
9:50 | 483 |  | 479 | 483 |  | 355 | 356 |  | 354 |  | 60 | 297.8139 | 182 | 59 |  | 99.27%
10:05 | 482 |  | 479 | 482 |  | 354 | 354 |  | 354 |  | 60 | 295.5277 | 183 | 58 |  | 98.51%
10:20 | 483 |  | 479 | 483 |  | 354 | 355 |  | 354 |  | 60 | 296.9774 | 183 | 58 |  | 98.99%
10:35 | 483 |  | 479 | 483 |  | 354 | 354 |  | 354 |  | 60 | 296.1408 | 184 | 58 |  | 98.71%
10:40 | 484 |  | 478 | 482 |  | 0 | 0 |  | 0 |  | 60 | 0 | 173 | 64 |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | #DIV/0!
Customer Witness Acceptance: | [7 empty] | MacAllister Engine Power Approval:
By: | [7 empty] | By:
Title: | [7 empty] | Title: |  | TECH
SMM/MEP/072800 | [15 empty] | Page 1 of | 1